## Shrawan
NEPAL ELECTRICITY AUTHORITY
DHARAN DISTRIBUTION CENTER
Peak Load Details
Month: | Shrawan | 2082
Day | 33KV Duhabi-Dharan |  |  |  | 33KV Dharan-Dhankuta |  |  |  | 33KV Dharan-Chatara Bayarban |  |  |  | 33/11KV, 16.6MVA Power Trf 1 |  | 11KV Incomer 1 |  | Dharan |  | Bagarkot |  | Local Chatara |  | BPKIHS |  | 33/11KV, 8MVA Power Trf 2 |  | 11KV Incomer 2 |  | Khanepani |  | Railway |  | British |  | Industrial |  | 33/11KV, 8MVA Power Trf 3 |  | 11KV Incomer 3 |  | Bhanu |  | Panmara
| Max. Import (A) | Time | Max. Export (A) | Time | Max. Import (A) | Time | Max. Export (A) | Time | Max. Import (A) | Time | Max. Export (A) | Time | Max. (A) | Time | Max. (A) | Time | Max. (A) | Time | Max. (A) | Time | Max. (A) | Time | Max. (A) | Time | Max. (A) | Time | Max. (A) | Time | Max. (A) | Time | Max. (A) | Time | Max. (A) | Time | Max. (A) | Time | Max. (A) | Time | Max. (A) | Time | Max. (A) | Time | Max. (A) | Time
1 | 388 | 19:30 |  |  |  |  | 45 | 7:00 |  |  | 1.2 | 19:30 | 206 | 19:30 | 569 | 19:30 | 172 | 19:30 | 156 | 19:30 | 250 | 19:30 | 41 | 10:00 | 60 | 21:00 | 171 | 21:00 | 53 | 12:00 | 75 | 20:00 | 34 | 21:00 | 42 | 10:00 | 83 | 19:30 | 250 | 19:30 | 166 | 19:30 | 68 | 20:00
2 | 418 | 20:00 |  |  |  |  | 21 | 19:30 |  |  | 1.7 | 12:00 | 208 | 20:00 | 579 | 20:00 | 182 | 19:30 | 157 | 20:00 | 247 | 20:00 | 41 | 9:00 | 79 | 20:00 | 215 | 20:00 | 54 | 16:00 | 128 | 20:00 | 35 | 21:00 | 54 | 8:00 | 86 | 20:00 | 239 | 20:00 | 181 | 11:00 | 70 | 19;30
3 | 410 | 19:30 |  |  |  |  | 21 | 19:30 |  |  | 1.2 | 18:30 | 223 | 19:30 | 620 | 19:30 | 191 | 19:30 | 157 | 19:30 | 259 | 19:30 | 24 | 12:00 | 61 | 19:30 | 172 | 19:30 | 51 | 14:00 | 76 | 19:30 | 37 | 19:30 | 15 | 9:00 | 85 | 19:00 | 246 | 19:00 | 178 | 19:00 | 67 | 19:00
4 | 360 | 20:00 |  |  |  |  | 18 | 19:30 |  |  | 1.2 | 18:30 | 190 | 19:30 | 532 | 19:30 | 157 | 19:30 | 141 | 20:00 | 222 | 19:30 | 39 | 20:00 | 56 | 20:00 | 163 | 20:00 | 48 | 6:00 | 70 | 21:00 | 33 | 21:00 | 45 | 11:00 | 72 | 19:30 | 209 | 19:00 | 150 | 19:00 | 61 | 19:30
5 | 406 | 19:30 |  |  |  |  | 18 | 19:30 |  |  | 1.3 | 19:30 | 213 | 19:30 | 591 | 19:30 | 180 | 19:30 | 159 | 19:30 | 251 | 19:30 | 39 | 11:00 | 66 | 16:00 | 187 | 16:00 | 51 | 19:30 | 75 | 20:00 | 36 | 20:00 | 48 | 9:00 | 86 | 19:30 | 242 | 19:30 | 171 | 19:30 | 72 | 20;00
6 | 400 | 19:30 |  |  |  |  | 20 | 19:30 |  |  | 6 | 8:00 | 207 | 19:30 | 571 | 19:30 | 182 | 19:30 | 156 | 20:00 | 251 | 19:30 | 45 | 9:00 | 71 | 19:30 | 201 | 19:30 | 51 | 5:00 | 74 | 19:30 | 67 | 16:00 | 46 | 16:00 | 85 | 19:30 | 237 | 19:30 | 165 | 19:00 | 71 | 19:30
7 | 425 | 19:30 |  |  |  |  | 18 | 19:30 |  |  | 1.3 | 19:30 | 227 | 19:30 | 626 | 19:30 | 192 | 19:30 | 169 | 20:00 | 267 | 19:30 | 39 | 12:00 | 69 | 8:00 | 192 | 8:00 | 55 | 19:30 | 76 | 19:00 | 71 | 9:00 | 38 | 9:00 | 88 | 19:30 | 263 | 19:00 | 188 | 19:00 | 78 | 19:30
8 | 444 | 20:00 |  |  |  |  | 20 | 19:30 |  |  | 1.4 | 18:30 | 239 | 19:30 | 637 | 19:30 | 195 | 19:00 | 175 | 20:00 | 274 | 19:30 | 45 | 10:00 | 67 | 20:00 | 187 | 20:00 | 50 | 6:00 | 80 | 20:00 | 42 | 21:00 | 45 | 11:00 | 98 | 19:00 | 267 | 19:00 | 192 | 19:00 | 74 | 19:00
9 | 406 | 20:00 |  |  |  |  | 20 | 19:00 | 16 | 14:00 | 6.1 | 13:00 | 219 | 19:30 | 614 | 19:30 | 187 | 19:30 | 163 | 19:30 | 263 | 19:30 | 43 | 10:00 | 65 | 20:00 | 184 | 20:00 | 50 | 19:30 | 79 | 20:00 | 36 | 20:00 | 55 | 11:00 | 90 | 19:30 | 260 | 19:30 | 187 | 19:30 | 71 | 19:30
10 | 373 | 19:30 |  |  |  |  | 20 | 19:30 | 14.9 | 22:00 |  |  | 208 | 20:00 | 566 | 20:00 | 175 | 19:30 | 159 | 21:00 | 246 | 21:00 | 21 | 10:00 | 54 | 11:00 | 153 | 11:00 | 50 | 4:00 | 73 | 21:00 | 36 | 20:00 | 21 | 9:00 | 86 | 21:00 | 227 | 21:00 | 164 | 21:00 | 65 | 19:30
11 | 367 | 19:30 |  |  |  |  | 16 | 21:00 | 13.5 | 9:00 |  |  | 203 | 19:30 | 561 | 19:30 | 175 | 19:00 | 153 | 20:00 | 238 | 19:30 | 43 | 10:00 | 68 | 19:30 | 177 | 19:30 | 50 | 21:00 | 69 | 20:00 | 38 | 21:00 | 56 | 14:00 | 83 | 19:30 | 234 | 19:30 | 185 | 14:00 | 65 | 19:30
12 | 371 | 19:30 |  |  |  |  | 20 | 19:30 | 12.6 | 8:00 |  |  | 200 | 19:30 | 557 | 19:30 | 167 | 19:30 | 149 | 19:30 | 237 | 19:30 | 42 | 10:00 | 68 | 19:30 | 179 | 19:30 | 52 | 8:00 | 73 | 19:30 | 34 | 21:00 | 52 | 16:00 | 77 | 19:30 | 219 | 19:30 | 157 | 19:30 | 62 | 19:30
13 | 396 | 19:30 |  |  |  |  | 19 | 21:00 | 13.6 | 17:00 |  |  | 215 | 19:30 | 604 | 19:30 | 183 | 19:30 | 163 | 20:00 | 257 | 19:30 | 42 | 9:00 | 67 | 19:30 | 185 | 19:30 | 50 | 13:00 | 77 | 19:30 | 37 | 21:00 | 55 | 10:00 | 84 | 19:30 | 238 | 19:30 | 169 | 19:30 | 68 | 19:30
14 | 380 | 19:30 |  |  |  |  | 19 | 19:30 | 20.4 | 22:00 |  |  | 206 | 19:30 | 571 | 19:30 | 180 | 19:30 | 157 | 21:00 | 238 | 20:00 | 43 | 10:00 | 64 | 21:00 | 178 | 21:00 | 51 | 21:00 | 74 | 20:00 | 49 | 20:00 | 49 | 10:00 | 84 | 19:00 | 231 | 19:00 | 167 | 19:00 | 66 | 19:30
15 | 390 | 19:30 |  |  |  |  | 19 | 19:30 | 15.8 | 8:00 |  |  | 212 | 19:30 | 586 | 19:30 | 179 | 19:30 | 158 | 21:00 | 249 | 19:30 | 43 | 10:00 | 64 | 19:30 | 180 | 19:30 | 50 | 8:00 | 69 | 21:00 | 37 | 20:00 | 54 | 10:00 | 84 | 19:30 | 226 | 19:30 | 168 | 19:30 | 68 | 21:00
16 | 354 | 19:30 |  |  |  |  | 19 | 19:30 | 14.6 | 18:30 |  |  | 197 | 19:30 | 556 | 19:30 | 176 | 19:00 | 152 | 20:00 | 236 | 20:00 | 43 | 9:00 | 59 | 8:00 | 170 | 8:00 | 52 | 8:00 | 69 | 20:00 | 33 | 21:00 | 41 | 11:00 | 79 | 19:00 | 226 | 19:00 | 162 | 19:00 | 66 | 20:00
17 | 352 | 19:30 |  |  |  |  | 18 | 19:30 | 18.4 | 8:00 |  |  | 208 | 19:30 | 590 | 19:30 | 174 | 19:30 | 156 | 20:00 | 238 | 19:30 | 22 | 11:00 | 48 | 19:30 | 141 | 19:30 | 48 | 6:00 | 71 | 19:30 | 31 | 22:00 | 13 | 11:00 | 79 | 19:30 | 226 | 19:30 | 156 | 19:30 | 66 | 19:30
18 | 369 | 19:30 |  |  |  |  | 34 | 12:00 | 15 | 19:00 |  |  | 196 | 19:30 | 521 | 19:30 | 158 | 19:30 | 139 | 19:30 | 220 | 19:30 | 41 | 8:00 | 59 | 13:00 | 172 | 13:00 | 53 | 13:00 | 66 | 20:00 | 29 | 7:00 | 60 | 11:00 | 76 | 19:00 | 208 | 19:00 | 167 | 10:00 | 58 | 19:30
19 | 338 | 19:30 |  |  |  |  | 17 | 19:30 | 15 | 9:00 |  |  | 189 | 19:30 | 524 | 19:30 | 157 | 19:30 | 146 | 21:00 | 224 | 20:00 | 42 | 11:00 | 54 | 19:30 | 143 | 19:30 | 49 | 5:00 | 68 | 19:30 | 31 | 21:00 | 47 | 9:00 | 78 | 19:30 | 216 | 19:30 | 152 | 19:00 | 71 | 19:30
20 | 345 | 19:30 |  |  |  |  | 18 | 19:30 | 17.5 | 23:00 | 1.9 | 19:00 | 198 | 19:30 | 565 | 19:30 | 167 | 19:30 | 147 | 19:30 | 235 | 19:30 | 38 | 11:00 | 56 | 13:00 | 145 | 13:00 | 31 | 12:00 | 67 | 20:00 | 30 | 19:30 | 50 | 14:00 | 78 | 19:00 | 225 | 19:00 | 161 | 19:00 | 66 | 19:30
21 | 336 | 19:30 |  |  |  |  | 18 | 19:30 | 16.4 | 20:00 |  |  | 195 | 19:30 | 557 | 19:30 | 167 | 19:00 | 150 | 19:30 | 228 | 19:30 | 39 | 11:00 | 55 | 19:30 | 156 | 11:00 | 28 | 6:00 | 68 | 19:30 | 31 | 21:00 | 56 | 16:00 | 79 | 19:00 | 224 | 19:00 | 162 | 19:00 | 64 | 20:00
22 | 352 | 19:00 |  |  |  |  | 18 | 19:00 | 14.8 | 10:00 |  |  | 187 | 19:00 | 524 | 19:00 | 159 | 19:00 | 145 | 19:30 | 220 | 19:00 | 41 | 11:00 | 58 | 19:30 | 163 | 19:30 | 30 | 14:00 | 69 | 19:30 | 30 | 19:00 | 52 | 9:00 | 78 | 19:00 | 222 | 19:00 | 158 | 18:30 | 64 | 19:00
23 | 341 | 19:30 |  |  |  |  | 19 | 19:00 | 15 | 19:30 |  |  | 187 | 19:30 | 512 | 19:30 | 161 | 19:00 | 141 | 20:00 | 220 | 20:00 | 38 | 10:00 | 56 | 20:00 | 157 | 20:00 | 60 | 23:00 | 69 | 19:30 | 28 | 20:00 | 52 | 11:00 | 73 | 19:00 | 216 | 19:00 | 155 | 19:00 | 61 | 19:00
24 | 346 | 20:00 |  |  |  |  | 19 | 20:00 | 18.5 | 18:00 |  |  | 192 | 19:30 | 505 | 19:30 | 156 | 19:00 | 139 | 19:00 | 216 | 19:00 | 22 | 8:00 | 58 | 20:00 | 146 | 20:00 | 40 | 16:00 | 68 | 20:00 | 30 | 19:30 | 16 | 17:00 | 79 | 19:00 | 211 | 19:00 | 150 | 19:00 | 67 | 20:00
25 | 360 | 19:30 |  |  |  |  | 20 | 19:30 | 16 | 2:00 | 1.2 | 12:00 | 194 | 19:00 | 549 | 19:00 | 163 | 19:00 | 149 | 20:00 | 234 | 19:30 | 36 | 10:00 | 55 | 19:00 | 166 | 19:00 | 61 | 23:00 | 71 | 19:00 | 31 | 19:30 | 38 | 10:00 | 77 | 19:30 | 231 | 19:00 | 163 | 19:00 | 67 | 19:00
26 | 350 | 19:00 |  |  |  |  | 20 | 19:00 | 17.1 | 17:30 |  |  | 195 | 19:30 | 540 | 19:30 | 164 | 19:00 | 149 | 20:00 | 227 | 19:30 | 37 | 10:00 | 55 | 19:00 | 155 | 19:00 | 34 | 5:00 | 67 | 19:30 | 33 | 19:30 | 42 | 13:00 | 78 | 19:00 | 218 | 19:00 | 155 | 19:00 | 65 | 19:30
27 | 361 | 19:00 |  |  |  |  | 19 | 17:00 | 15 | 19:00 |  |  | 203 | 19:30 | 551 | 19:30 | 167 | 19:00 | 149 | 19:30 | 234 | 19:30 | 37 | 11:00 | 58 | 13:00 | 158 | 13:00 | 35 | 8:00 | 72 | 19:30 | 34 | 20:00 | 48 | 16:00 | 81 | 19:00 | 230 | 19:00 | 164 | 19:00 | 66 | 19:30
28 | 302 | 20:00 |  |  |  |  | 16 | 19:00 | 22.7 | 19:00 | 1.4 | 7:00 | 172 | 19:00 | 475 | 19:00 | 146 | 19:00 | 133 | 19:30 | 194 | 19:00 | 37 | 11:00 | 58 | 20:00 | 163 | 20:00 | 50 | 8:00 | 66 | 19:30 | 29 | 19:30 | 52 | 10:00 | 70 | 19:00 | 198 | 19:00 | 143 | 19:00 | 55 | 19:00
29 | 325 | 19:30 |  |  |  |  | 21 | 19:30 | 23 | 19:30 |  |  | 180 | 19:30 | 501 | 19:30 | 153 | 19:30 | 135 | 20:00 | 2120 | 19:30 | 35 | 11:00 | 65 | 13:00 | 182 | 13:00 | 39 | 6:00 | 100 | 14:00 | 30 | 19:30 | 45 | 10:00 | 79 | 19:00 | 209 | 19:00 | 151 | 19:00 | 62 | 19:30
30 | 360 | 18:30 |  |  |  |  | 52 | 11:00 | 20.6 | 13:00 |  |  | 198 | 19:00 | 537 | 19:00 | 167 | 19:00 | 148 | 19;30 | 225 | 19:30 | 41 | 11:00 | 55 | 19:30 | 157 | 19:30 | 29 | 1:00 | 68 | 19:00 | 29 | 20:00 | 45 | 16:00 | 82 | 19:00 | 235 | 19:00 | 170 | 19:00 | 65 | 19:30
31 | 369 | 19:00 |  |  |  |  | 21 | 19:00 | 22.9 | 20:00 |  |  | 200 | 19:30 | 559 | 19:30 | 166 | 19:30 | 155 | 19:30 | 241 | 19:30 | 21 | 12:00 | 58 | 19:30 | 156 | 19:30 | 34 | 10:00 | 72 | 20:00 | 31 | 21:00 | 16 | 12:00 | 89 | 19:00 | 231 | 19:00 | 163 | 19:00 | 69 | 19:00
32
Monthly | 444 |  | 0 |  | 0 |  | 52 |  | 23 |  | 6.1 |  | 239 |  | 637 |  | 195 |  | 175 |  | 2120 |  | 45 |  | 79 |  | 215 |  | 61 |  | 128 |  | 71 |  | 60 |  | 98 |  | 267 |  | 192 |  | 78
…………….. …………….. ……………..
Prepared by Checked by Approved by

## Bhadra
NEPAL ELECTRICITY AUTHORITY
DHARAN DISTRIBUTION CENTER
Peak Load Details
Month: | Bhadra | 2082
Day | 33KV Duhabi-Dharan |  |  |  | 33KV Dharan-Dhankuta |  |  |  | 33KV Dharan-Chatara Bayarban |  |  |  | 33/11KV, 16.6MVA Power Trf 1 |  | 11KV Incomer 1 |  | Dharan |  | Bagarkot |  | Local Chatara |  | BPKIHS |  | 33/11KV, 8MVA Power Trf 2 |  | 11KV Incomer 2 |  | Khanepani |  | Railway |  | British |  | Industrial |  | 33/11KV, 8MVA Power Trf 3 |  | 11KV Incomer 3 |  | Bhanu |  | Panmara
| Max. Import (A) | Time | Max. Export (A) | Time | Max. Import (A) | Time | Max. Export (A) | Time | Max. Import (A) | Time | Max. Export (A) | Time | Max. (A) | Time | Max. (A) | Time | Max. (A) | Time | Max. (A) | Time | Max. (A) | Time | Max. (A) | Time | Max. (A) | Time | Max. (A) | Time | Max. (A) | Time | Max. (A) | Time | Max. (A) | Time | Max. (A) | Time | Max. (A) | Time | Max. (A) | Time | Max. (A) | Time | Max. (A) | Time
1 | 369 | 19:00 |  |  |  |  | 17 | 7:00 | 36 | 19:00 |  |  | 211 | 19:00 | 592 | 19:00 | 178 | 19:00 | 157 | 19:30 | 250 | 19:00 | 38 | 11:00 | 57 | 11:00 | 157 | 11:00 | 34 | 11:00 | 73 | 19:00 | 52 | 14:00 | 38 | 9:00 | 86 | 19:00 | 249 | 19:00 | 175 | 19:00 | 70 | 19:00
2 | 310 | 19:30 | [6 empty] | 23.8 | 12:00 |  |  | 196 | 19:30 | 535 | 19:30 | 168 | 19:00 | 147 | 20:00 | 228 | 19:30 | 42 | 10:00 | 51 | 12:00 | 142 | 19:00 | 32 | 12:00 | 66 | 19:30 | 32 | 19:30 | 47 | 11:00 | 81 | 19:00 | 225 | 19:00 | 160 | 19:00 | 65 | 19:00
3 | 326 | 19:30 |  |  |  |  | 8 | 17:00 | 23 | 10:00 |  |  | 189 | 19:30 | 523 | 19:30 | 158 | 19:00 | 141 | 20:00 | 218 | 19:30 | 40 | 10:00 | 57 | 20:00 | 160 | 20:00 | 39 | 7:00 | 67 | 19:00 | 32 | 20:00 | 49 | 16:00 | 78 | 19:00 | 221 | 19:00 | 162 | 19:00 | 60 | 19:30
4 | 350 | 19:00 |  |  |  |  | 18 | 19:00 | 21 | 4:00 |  |  | 200 | 19:00 | 555 | 19:00 | 172 | 19:00 | 148 | 19:00 | 233 | 19:00 | 39 | 10:00 | 53 | 13:00 | 153 | 13:00 | 35 | 8:00 | 72 | 19:30 | 31 | 19:30 | 56 | 14:00 | 81 | 19:00 | 232 | 19:00 | 167 | 19:00 | 64 | 19:00
5 | 345 | 19:00 |  |  |  |  | 17 | 19:00 | 18 | 1:00 |  |  | 200 | 19:00 | 547 | 19:00 | 168 | 19:00 | 148 | 19:00 | 230 | 19:30 | 39 | 10:00 | 56 | 12:00 | 150 | 12:00 | 39 | 5:00 | 63 | 20:00 | 33 | 21:00 | 52 | 19:00 | 81 | 19:00 | 229 | 19:00 | 166 | 19:00 | 63 | 19:00
6 | 355 | 19:00 |  |  |  |  | 20 | 19:30 | 18.2 | 19:00 |  |  | 200 | 19:00 | 567 | 19:00 | 169 | 19:00 | 151 | 19:30 | 234 | 19:30 | 38 | 11:00 | 58 | 11:00 | 164 | 11:00 | 35 | 11:00 | 69 | 19:00 | 30 | 19:30 | 60 | 9:00 | 81 | 19:00 | 232 | 19:00 | 168 | 19:00 | 64 | 19:00
7 | 346 | 19:30 |  |  |  |  | 22 | 19:30 | 17 | 3:00 |  |  | 196 | 19:30 | 539 | 19:30 | 169 | 19:30 | 146 | 21:00 | 236 | 19:30 | 20 | 8:00 | 50 | 19:30 | 141 | 19:30 | 36 | 6:00 | 71 | 19:00 | 30 | 21:00 | 23 | 15:00 | 82 | 19:30 | 226 | 19:00 | 159 | 19:30 | 63 | 19:00
8 | 369 | 19:00 |  |  |  |  | 26 | 19:00 | 13.4 | 13:00 |  |  | 206 | 19:00 | 543 | 19:00 | 170 | 19:00 | 149 | 21:00 | 228 | 19:00 | 39 | 15:00 | 58 | 10:00 | 157 | 10:00 | 40 | 9:00 | 70 | 19:30 | 31 | 20:00 | 62 | 10:00 | 86 | 19:00 | 227 | 19:00 | 164 | 19:00 | 63 | 19:00
9 | 360 | 19:00 |  |  |  |  | 19 | 19:00 | 13.9 | 19:00 |  |  | 202 | 19:00 | 552 | 19:00 | 170 | 19:00 | 147 | 19:30 | 234 | 19:00 | 48 | 13:00 | 59 | 13:00 | 156 | 13:00 | 34 | 5:00 | 70 | 19:00 | 31 | 19:30 | 49 | 11:00 | 80 | 19:00 | 227 | 19:00 | 164 | 19:00 | 65 | 19:30
10 | 337 | 19:00 |  |  |  |  | 19 | 19:00 | 18.3 | 8:00 |  |  | 186 | 19:00 | 512 | 19:00 | 156 | 19:00 | 138 | 19:30 | 213 | 19:00 | 37 | 10:00 | 58 | 10:00 | 189 | 10:00 | 32 | 5:00 | 68 | 19:30 | 30 | 19:30 | 48 | 9:00 | 80 | 19:00 | 214 | 19:00 | 151 | 19:00 | 61 | 19:00
11 | 338 | 18:30 |  |  |  |  | 18 | 18:30 | 19.6 | 22:00 |  |  | 190 | 19:30 | 525 | 19:30 | 158 | 19:00 | 138 | 19:30 | 219 | 19:00 | 38 | 10:00 | 52 | 19:00 | 142 | 19:00 | 34 | 12:00 | 65 | 19:00 | 31 | 19:00 | 48 | 11:00 | 75 | 19:00 | 208 | 19:00 | 149 | 19:00 | 59 | 18:30
12 | 350 | 19:00 |  |  |  |  | 18 | 19:00 | 16.4 | 13:00 |  |  | 194 | 19:00 | 519 | 19:00 | 167 | 19:00 | 140 | 19:00 | 228 | 19:00 | 40 | 11:00 | 54 | 19:00 | 150 | 19:00 | 32 | 6:00 | 72 | 19:00 | 30 | 20:00 | 53 | 16:00 | 78 | 19:00 | 225 | 19:00 | 163 | 19:00 | 63 | 19:00
13 | 337 | 19:00 |  |  |  |  | 20 | 19:00 | 20.3 | 16:00 |  |  | 193 | 19:00 | 536 | 19:00 | 164 | 19:00 | 143 | 19:00 | 226 | 19:00 | 35 | 10:00 | 52 | 9:00 | 149 | 9:00 | 33 | 12:00 | 69 | 19:00 | 31 | 20:00 | 48 | 16:00 | 78 | 19:30 | 222 | 19:30 | 160 | 19:30 | 62 | 19:00
14 | 323 | 19:00 |  |  |  |  | 20 | 19:00 | 20 | 8:00 |  |  | 188 | 19:00 | 518 | 19:00 | 159 | 19:00 | 141 | 19:00 | 218 | 19:00 | 19 | 11:00 | 39 | 19:30 | 107 | 19:30 | 35 | 5:00 | 69 | 19:30 | 31 | 21:00 | 14 | 10:00 | 76 | 19:00 | 213 | 19:00 | 153 | 18:30 | 62 | 19:30
15 | 360 | 19:00 |  |  |  |  | 20 | 19:00 | 20.9 | 20:00 |  |  | 205 | 19:00 | 565 | 19:00 | 173 | 18:30 | 153 | 19:00 | 236 | 19:00 | 40 | 10:00 | 57 | 11:00 | 158 | 11:00 | 45 | 6:00 | 70 | 20:00 | 32 | 19:00 | 48 | 9:00 | 84 | 19:00 | 239 | 19:00 | 172 | 19:00 | 66 | 19:00
16 | 382 | 19:00 |  |  |  |  | 20 | 19:00 | 21.7 | 12:00 |  |  | 220 | 19:00 | 610 | 19:00 | 183 | 19:00 | 162 | 19:00 | 260 | 19:00 | 42 | 10:00 | 60 | 16:00 | 163 | 16:00 | 35 | 14:00 | 77 | 19:00 | 35 | 19:30 | 53 | 9:00 | 88 | 19:00 | 249 | 19:00 | 179 | 19:00 | 70 | 19:00
17 | 376 | 19:00 |  |  |  |  | 20 | 19:00 | 20 | 16:00 |  |  | 212 | 19:00 | 581 | 19:00 | 178 | 19:00 | 155 | 19:00 | 245 | 19:00 | 42 | 10:00 | 64 | 16:00 | 174 | 16:00 | 44 | 14:00 | 79 | 19:00 | 34 | 19:30 | 52 | 16:00 | 89 | 19:00 | 251 | 19:00 | 180 | 19:00 | 70 | 19:00
18 | 377 | 19:00 |  |  |  |  | 19 | 19:00 | 25.5 | 23:00 |  |  | 215 | 19:00 | 588 | 19:00 | 182 | 18:30 | 160 | 19:30 | 243 | 19:00 | 41 | 10:00 | 68 | 21:00 | 193 | 21:00 | 33 | 6:00 | 133 | 21:00 | 36 | 18:30 | 54 | 16:00 | 90 | 19:00 | 253 | 19:00 | 185 | 19:00 | 68 | 19:30
19 | 374 | 19:00 |  |  |  |  | 20 | 19:30 | 22.6 | 1:00 |  |  | 212 | 19:00 | 594 | 19:00 | 181 | 19:00 | 160 | 19:30 | 252 | 19:00 | 44 | 11:00 | 78 | 8:00 | 212 | 8:00 | 33 | 8:00 | 114 | 7:00 | 35 | 20:00 | 61 | 9:00 | 88 | 19:00 | 248 | 19:00 | 180 | 19:00 | 70 | 19:00
20 | 380 | 19:00 |  |  |  |  | 20 | 19:00 | 19.4 | 19:30 |  |  | 207 | 18:30 | 577 | 18:30 | 178 | 18:30 | 152 | 18:30 | 232 | 19:30 | 43 | 11:00 | 53 | 11:00 | 155 | 11:00 | 34 | 11:00 | 66 | 18:30 | 44 | 21:00 | 60 | 9:00 | 86 | 18:30 | 247 | 18:30 | 180 | 19:00 | 69 | 18:30
21 | 355 | 18:00 |  |  |  |  | 50 | 15:00 | 23.5 | 13:00 |  |  | 210 | 18:30 | 580 | 18:30 | 179 | 18:30 | 152 | 18:30 | 237 | 18:30 | 23 | 16:00 | 56 | 11:00 | 154 | 11:00 | 35 | 7:00 | 67 | 18:30 | 46 | 8:00 | 26 | 11:00 | 86 | 18:30 | 244 | 18:30 | 176 | 18:30 | 69 | 18:30
22 | 349 | 19:00 |  |  |  |  | 19 | 19:00 | 21.9 | 10:00 |  |  | 187 | 19:00 | 530 | 19:00 | 175 | 19:00 | 144 | 20:00 | 227 | 19:00 | 12 | 6:00 | 63 | 8:00 | 182 | 8:00 | 33 | 5:00 | 67 | 19:30 | 61 | 9:00 | 56 | 11:00 | 78 | 19:00 | 223 | 19:00 | 162 | 19:00 | 61 | 19:00
23 | 347 | 19:00 |  |  |  |  | 29 | 12:00 | 22.8 | 3:00 |  |  | 189 | 19:00 | 518 | 19:00 | 169 | 19:00 | 139 | 19:00 | 223 | 19:00 |  |  | 64 | 19:30 | 186 | 23:00 | 33 | 12:00 | 64 | 19:30 | 63 | 10:00 | 51 | 16:00 | 77 | 19:00 | 220 | 19:00 | 158 | 19:00 | 61 | 19:00
24 | 310 | 18:30 |  |  |  |  | 19 | 19:00 | 22.4 | 12:00 |  |  | 186 | 18:30 | 510 | 18:30 | 147 | 18:30 | 134 | 18:30 | 212 | 18:30 | 36 | 12:00 | 66 | 8:00 | 188 | 7:00 | 34 | 12:00 | 98 | 1:00 | 63 | 10:00 | 50 | 10:00 | 68 | 11:00 | 185 | 11:00 | 145 | 11:00 | 61 | 18:30
25 | 300 | 18:30 | [6 empty] | 21.6 | 18:30 |  |  | 189 | 18:30 | 522 | 18:30 | 141 | 18:30 | 143 | 18:30 | 223 | 18:30 | 33 | 9:00 | 55 | 19:00 | 145 | 19:00 | 39 | 14:00 | 65 | 18:30 | 33 | 18:30 | 44 | 15:00 | 68 | 18:30 | 190 | 18:30 | 124 | 18:30 | 65 | 18:30
26 | 331 | 19:30 | [6 empty] | 22.2 | 21:00 |  |  | 171 | 18:30 | 477 | 18:30 | 140 | 18:30 | 131 | 19:00 | 219 | 19:00 | 39 | 9:00 | 59 | 10:00 | 161 | 10:00 | 38 | 9:00 | 57 | 11:00 | 31 | 18:30 | 45 | 9:00 | 64 | 18:00 | 179 | 18:00 | 124 | 18:30 | 56 | 19:00
27 | 316 | 18:30 |  |  |  |  | 17 | 18:30 | 20.6 | 10:00 |  |  | 188 | 19:00 | 521 | 19:00 | 145 | 18:30 | 147 | 19:00 | 222 | 19:30 | 37 | 9:00 | 49 | 19:30 | 141 | 19:30 | 36 | 1:00 | 61 | 18:30 | 32 | 19:00 | 50 | 11:00 | 74 | 19:30 | 189 | 19:30 | 134 | 18:00 | 64 | 19:00
28 | 291 | 19:00 |  |  |  |  | 33 | 11:00 | 22.8 | 13:00 |  |  | 179 | 18:30 | 488 | 18:30 | 140 | 18:30 | 136 | 19:00 | 211 | 18:30 | 21 | 12:00 | 56 | 19:30 | 150 | 19:30 | 31 | 23:00 | 70 | 18:30 | 29 | 19:00 | 18 | 11:00 | 70 | 18:30 | 190 | 18:30 | 132 | 18:30 | 62 | 18:30
29 | 318 | 19:30 |  |  |  |  | 22 | 18:00 | 23.8 | 19:00 |  |  | 181 | 18:30 | 499 | 18:30 | 155 | 18:30 | 132 | 19:00 | 216 | 18:30 | 38 | 10:00 | 54 | 9:00 | 151 | 9:00 | 41 | 11:00 | 96 | 18:30 | 31 | 19:30 | 49 | 9:00 | 74 | 18:30 | 216 | 18:30 | 150 | 18:30 | 60 | 18:30
30 | 335 | 18:30 |  |  |  |  | 17 | 10:00 | 23 | 20:00 |  |  | 177 | 18:30 | 487 | 18:30 | 153 | 18:30 | 127 | 18:30 | 202 | 18:30 | 39 | 11:00 | 55 | 12:00 | 150 | 12:00 | 44 | 14:00 | 62 | 18:30 | 27 | 18:30 | 52 | 10:00 | 73 | 18:30 | 204 | 18:30 | 149 | 18:30 | 55 | 18:30
31 | 306 | 19:00 |  |  |  |  | 18 | 18:30 | 21.3 | 8:00 |  |  | 174 | 18:30 | 475 | 18:30 | 145 | 19:00 | 130 | 19:00 | 204 | 18:30 | 37 | 11:00 | 52 | 21:00 | 149 | 21:00 | 31 | 11:00 | 60 | 18:30 | 27 | 19:00 | 30 | 7:00 | 75 | 18:30 | 207 | 18:30 | 151 | 18:30 | 56 | 18:30
32
Monthly | 382 |  | 0 |  | 0 |  | 50 |  | 36 |  | 0 |  | 220 |  | 610 |  | 183 |  | 162 |  | 260 |  | 48 |  | 78 |  | 212 |  | 45 |  | 133 |  | 63 |  | 62 |  | 90 |  | 253 |  | 185 |  | 70
…………….. …………….. ……………..
Prepared by Checked by Approved by

## Ashoj
NEPAL ELECTRICITY AUTHORITY
DHARAN DISTRIBUTION CENTER
Peak Load Details
Month: | Ashoj | 2082
Day | 33KV Duhabi-Dharan |  |  |  | 33KV Dharan-Dhankuta |  |  |  | 33KV Dharan-Chatara Bayarban |  |  |  | 33/11KV, 16.6MVA Power Trf 1 |  | 11KV Incomer 1 |  | Dharan |  | Bagarkot |  | Local Chatara |  | BPKIHS |  | 33/11KV, 8MVA Power Trf 2 |  | 11KV Incomer 2 |  | Khanepani |  | Railway |  | British |  | Industrial |  | 33/11KV, 8MVA Power Trf 3 |  | 11KV Incomer 3 |  | Bhanu |  | Panmara
| Max. Import (A) | Time | Max. Export (A) | Time | Max. Import (A) | Time | Max. Export (A) | Time | Max. Import (A) | Time | Max. Export (A) | Time | Max. (A) | Time | Max. (A) | Time | Max. (A) | Time | Max. (A) | Time | Max. (A) | Time | Max. (A) | Time | Max. (A) | Time | Max. (A) | Time | Max. (A) | Time | Max. (A) | Time | Max. (A) | Time | Max. (A) | Time | Max. (A) | Time | Max. (A) | Time | Max. (A) | Time | Max. (A) | Time
1 | 350 | 18:30 |  |  |  |  | 19 | 19:00 | 26.7 | 14:00 |  |  | 191 | 19:00 | 532 | 19:00 | 158 | 18:30 | 139 | 18:30 | 226 | 19:00 | 23 | 13:00 | 64 | 19:00 | 180 | 19:00 | 35 | 8:00 | 114 | 19:00 | 30 | 19:00 | 7 | 6:00 | 74 | 18:30 | 206 | 18:30 | 146 | 18:30 | 61 | 18:30
2 | 331 | 18:30 |  |  |  |  | 18 | 18:30 | 24.5 | 19:00 |  |  | 176 | 18:30 | 493 | 18:30 | 146 | 18:30 | 131 | 18:30 | 210 | 18:30 | 37 | 11:00 | 64 | 15:00 | 176 | 15:00 | 34 | 6:00 | 110 | 18:30 | 27 | 19:00 | 37 | 13:00 | 74 | 18:30 | 210 | 18:30 | 153 | 18:30 | 58 | 18:30
3 | 338 | 18:30 |  |  |  |  | 22 | 18:30 | 21.2 | 13:00 |  |  | 180 | 18:30 | 500 | 18:30 | 151 | 18:30 | 136 | 19:00 | 213 | 18:30 | 20 | 9:00 | 63 | 19:30 | 177 | 19:30 | 35 | 7:00 | 104 | 19:30 | 26 | 20:00 | 45 | 9:00 | 76 | 18:30 | 213 | 18:30 | 150 | 18:30 | 61 | 18:30
4 | 364 | 18:30 |  |  |  |  | 19 | 18:30 | 22.3 | 18:30 |  |  | 188 | 19:00 | 539 | 19:00 | 160 | 18:30 | 142 | 19:00 | 228 | 19:00 | 19 | 12:00 | 74 | 18:30 | 216 | 18:30 | 32 | 6:00 | 141 | 18:30 | 29 | 19:00 | 20 | 11:00 | 83 | 18:30 | 232 | 18:30 | 163 | 18:30 | 69 | 18:30
5 | 379 | 18:30 |  |  |  |  | 26 | 18:30 | 21.5 | 9:00 |  |  | 199 | 18:30 | 535 | 18:30 | 163 | 18:30 | 141 | 18:30 | 226 | 18:30 | 40 | 10:00 | 67 | 18:30 | 173 | 18:30 | 34 | 8:00 | 123 | 18:30 | 28 | 19:30 | 43 | 11:00 | 94 | 18:30 | 257 | 18:30 | 175 | 18:30 | 81 | 18:30
6 | 374 | 18:30 |  |  |  |  | 20 | 18:30 | 18.6 | 18:30 |  |  | 201 | 18:30 | 559 | 18:30 | 170 | 18:30 | 150 | 19:30 | 236 | 18:30 | 48 | 11:00 | 65 | 19:30 | 191 | 19:30 | 35 | 6:00 | 128 | 18:30 | 31 | 19:30 | 36 | 9:00 | 85 | 18:30 | 238 | 18:30 | 168 | 18:30 | 69 | 18:30
7 | 325 | 18:30 |  |  |  |  | 21 | 8:00 | 25.4 | 18:30 |  |  | 194 | 18:30 | 542 | 18:30 | 167 | 18:30 | 134 | 19:00 | 224 | 18:30 | 39 | 10:00 | 65 | 16:00 | 187 | 16:00 | 35 | 8:00 | 125 | 18:30 | 29 | 19:00 | 45 | 9:00 | 76 | 18:30 | 211 | 18:30 | 165 | 18:30 | 49 | 19:00
8 | 435 | 18:30 |  |  |  |  | 105 | 18:00 | 24.9 | 16:00 |  |  | 201 | 18:30 | 560 | 18:30 | 166 | 18:30 | 146 | 18:30 | 231 | 18:30 | 38 | 11:00 | 64 | 12:00 | 178 | 12:00 | 26 | 6:00 | 106 | 12:00 | 29 | 18:30 | 43 | 10:00 | 87 | 18:30 | 249 | 18:30 | 178 | 18:00 | 73 | 18:30
9 | 380 | 19:00 |  |  |  |  | 55 | 5:00 | 22.9 | 11:00 |  |  | 214 | 18:30 | 589 | 18:30 | 178 | 19:00 | 159 | 18:30 | 255 | 18:30 | 38 | 10:00 | 54 | 16:00 | 154 | 16:00 | 29 | 11:00 | 84 | 18:30 | 30 | 19:30 | 47 | 9:00 | 89 | 18:30 | 266 | 18:30 | 189 | 18:30 | 71 | 18:30
10 | 370 | 18:30 |  |  |  |  | 20 | 18:30 | 19 | 1:00 |  |  | 208 | 18:30 | 581 | 18:30 | 175 | 19:00 | 158 | 18:30 | 253 | 18:30 | 38 | 11:00 | 54 | 12:00 | 154 | 12:00 | 26 | 3:00 | 110 | 19:30 | 28 | 20:00 | 47 | 16:00 | 86 | 19:00 | 246 | 19:00 | 177 | 19:00 | 68 | 18:30
11 | 366 | 18:30 |  |  |  |  | 21 | 18:30 | 17 | 2:00 |  |  | 202 | 18:30 | 571 | 18:30 | 173 | 18:30 | 160 | 19:00 | 250 | 18:30 | 26 | 16:00 | 54 | 19:00 | 160 | 19:00 | 36 | 12:00 | 91 | 19:00 | 26 | 18:30 | 28 | 12:00 | 86 | 18:30 | 260 | 18:30 | 189 | 18:30 | 71 | 18:30
12 | 362 | 19:00 |  |  |  |  | 22 | 18:30 | 17.3 | 18:00 |  |  | 193 | 18:30 | 526 | 18:30 | 162 | 19:00 | 143 | 21:00 | 225 | 18:30 | 36 | 11:00 | 56 | 11:00 | 157 | 11:00 | 37 | 6:00 | 82 | 18:30 | 24 | 19:00 | 43 | 9:00 | 89 | 18:30 | 245 | 18:30 | 176 | 18:30 | 67 | 18:30
13 | 350 | 18:30 |  |  |  |  | 19 | 18:00 | 15.4 | 8:00 |  |  | 198 | 19:00 | 559 | 19:00 | 167 | 19:00 | 147 | 19:00 | 235 | 18:30 | 36 | 9:00 | 49 | 14:00 | 139 | 11:00 | 39 | 7:00 | 87 | 18:30 | 21 | 14:00 | 12 | 10:00 | 82 | 18:30 | 239 | 18:30 | 168 | 18:30 | 71 | 18:30
14 | 340 | 18:30 |  |  |  |  | 18 | 18:30 | 13.8 | 18:30 |  |  | 193 | 18:30 | 534 | 18:30 | 160 | 18:30 | 149 | 19:00 | 232 | 18:30 | 22 | 11:00 | 47 | 18:30 | 135 | 19:00 | 35 | 7:00 | 84 | 18:30 | 20 | 19:30 | 10 | 1:00 | 84 | 18:30 | 235 | 18:30 | 164 | 19:00 | 72 | 18:30
15 | 294 | 18:30 |  |  |  |  | 19 | 18:30 | 15 | 17:30 |  |  | 168 | 19:00 | 469 | 19:00 | 136 | 18:30 | 127 | 19:00 | 193 | 18:30 | 20 | 9:00 | 45 | 12:00 | 125 | 12:00 | 37 | 6:00 | 74 | 18:30 | 18 | 21:00 | 9 | 9:00 | 70 | 18:30 | 196 | 18:30 | 133 | 18:30 | 62 | 18:30
16 | 280 | 18:30 |  |  |  |  | 18 | 18:30 | 21.2 | 17:00 |  |  | 159 | 18:00 | 428 | 18:30 | 117 | 19:00 | 118 | 18:30 | 183 | 18:30 | 18 | 7:00 | 48 | 19:00 | 130 | 19:00 | 39 | 19:00 | 72 | 19:30 | 17 | 20:00 | 6 | 9:00 | 61 | 19:00 | 171 | 19:00 | 113 | 19:00 | 60 | 18:30
17 | 259 | 19:30 |  |  |  |  | 22 | 18:00 | 18.7 | 10:00 |  |  | - | - | - | - | - | - | - | - | 185 | 19:30 | - | - | 144 | 18:00 | 331 | 19:00 | 38 | 13:00 | 113 | 18:30 | 32 | 12:00 | 12 | 16:00 | 134 | 22:00 | 376 | 22:00 | 240 | 19:00 | 189 | 22:00
18 | 262 | 18:00 |  |  |  |  | 16 | 18:30 | 12.1 | 10:00 | 1.3 | 17:30 | - | - | - | - | - | - | - | - | 192 | 18:00 | - | - | 112 | 18:00 | 320 | 18:00 | 37 | 7:00 | 99 | 18:00 | 33 | 10:00 | 8 | 7:00 | 121 | 18:00 | 345 | 18:00 | 185 | 18:00 | 155 | 18:00
19 | 246 | 18:00 |  |  |  |  | 69 | 21:00 |  |  | 1.2 | 21:00 | 141 | 18:00 | 415 | 19:00 | 131 | 19:00 | 113 | 18:00 | 191 | 16:00 | 16 | 17:00 | 103 | 11:00 | 229 | 11:00 | 34 | 11:00 | 68 | 10:00 | 44 | 10:00 | 18 | 19:30 | 125 | 11:00 | 339 | 11:00 | 270 | 9:00 | 131 | 13:00
20 | 272 | 18:00 |  |  |  |  | 18 | 19:30 |  |  | 1.7 | 18:30 | 150 | 18:30 | 466 | 8:30 | 130 | 18:00 | 126 | 18:30 | 199 | 18:30 | 28 | 11:00 | 44 | 16:00 | 131 | 16:00 | 37 | 7:00 | 63 | 18:00 | 23 | 18:30 | 38 | 9:00 | 63 | 18:00 | 183 | 18:00 | 131 | 18:00 | 63 | 18:30
21 | 325 | 18:30 |  |  |  |  | 20 | 18:30 |  |  | 1.4 | 9:00 | 170 | 18:30 | 515 | 18:30 | 170 | 18:30 | 131 | 18:30 | 205 | 18:30 | 32 | 10:00 | 49 | 20:00 | 138 | 20:00 | 26 | 5:00 | 65 | 18:30 | 20 | 18:30 | 46 | 9:00 | 73 | 18:30 | 205 | 18:30 | 143 | 18:30 | 65 | 18:30
22 | 320 | 18:30 |  |  |  |  | 20 | 19:00 |  |  | 1.3 | 8:00 | 170 | 18:30 | 512 | 18:30 | 149 | 18:00 | 121 | 18:00 | 213 | 18:30 | 33 | 10:00 | 51 | 19:00 | 144 | 19:00 | 30 | 8:00 | 67 | 18:00 | 22 | 19:30 | 51 | 11:00 | 73 | 18:00 | 205 | 18:00 | 142 | 18:00 | 63 | 18:30
23 | 390 | 18:30 |  |  |  |  | 58 | 18:00 |  |  | 1.2 | 18:30 | 189 | 18:30 | 543 | 18:30 | 166 | 19:00 | 149 | 19:00 | 226 | 19:00 | 40 | 10:00 | 53 | 12:00 | 149 | 12:00 | 26 | 6:00 | 70 | 18:00 | 24 | 20:00 | 59 | 9:00 | 82 | 18:30 | 221 | 18:30 | 156 | 17:30 | 68 | 18:30
24 | 352 | 18:30 |  |  |  |  | 38 | 10:00 |  |  | 1.4 | 23:00 | 172 | 18:30 | 535 | 18:30 | 157 | 18:30 | 139 | 18:30 | 224 | 18:30 | 39 | 11:00 | 54 | 10:00 | 162 | 10:00 | 33 | 8:00 | 71 | 18:00 | 24 | 18:30 | 61 | 10:00 | 77 | 18:30 | 216 | 18:30 | 152 | 18:30 | 67 | 18:30
25 | 317 | 18:30 |  |  |  |  | 18 | 18:00 |  |  | 1.3 | 18:00 | 165 | 18:30 | 522 | 18:30 | 147 | 18:30 | 141 | 19:00 | 216 | 18:30 | 24 | 11:00 | 48 | 18:30 | 141 | 18:30 | 36 | 15:00 | 71 | 18:30 | 23 | 20:00 | 23 | 10:00 | 72 | 18:30 | 222 | 18:30 | 156 | 18:30 | 67 | 18:30
26 | 346 | 18:30 |  |  |  |  | 10 | 1:00 |  |  | 1.2 | 13:00 | 189 | 18:30 | 559 | 18:30 | 167 | 18:00 | 155 | 18:00 | 236 | 18:30 | 25 | 17:00 | 65 | 13:00 | 183 | 13:00 | 36 | 11:00 | 69 | 18:00 | 57 | 10:00 | 49 | 11:00 | 88 | 10:00 | 245 | 10:00 | 166 | 18:00 | 69 | 18:00
27 | 313 | 18:30 |  |  |  |  | 5 | 18:00 |  |  | 1.2 | 7:00 | 171 | 18:30 | 507 | 18:30 | 151 | 18:30 | 137 | 18:30 | 210 | 18:30 | 39 | 10:00 | 55 | 19:00 | 157 | 19:00 | 31 | 19:00 | 66 | 18:30 | 23 | 19:30 | 59 | 14:00 | 74 | 18:30 | 209 | 18:30 | 148 | 17:30 | 62 | 18:00
28 | 321 | 18:30 |  |  |  |  | 20 | 18:00 |  |  | 1.2 | 4:00 | 170 | 18:30 | 502 | 18:30 | 152 | 18:30 | 137 | 18:30 | 207 | 18:30 | 37 | 9:00 | 59 | 9:00 | 148 | 9:00 | 34 | 7:00 | 62 | 18:30 | 23 | 19:00 | 56 | 9:00 | 75 | 18:00 | 212 | 18:00 | 150 | 18:00 | 63 | 18:00
29 | 325 | 18:30 |  |  |  |  | 21 | 18:30 |  |  | 1.2 | 18:30 | 170 | 18:30 | 504 | 18:30 | 148 | 18:30 | 140 | 18:30 | 207 | 18:30 | 39 | 11:00 | 55 | 19:00 | 155 | 19:00 | 35 | 22:00 | 67 | 18:30 | 22 | 18:00 | 52 | 11:00 | 75 | 18:00 | 212 | 18:00 | 151 | 18:30 | 66 | 18:00
30 | 354 | 18:30 |  |  |  |  | 21 | 18:30 |  |  | 1.4 | 9:00 | 178 | 18:30 | 523 | 18:30 | 161 | 18:00 | 144 | 18:30 | 216 | 18:00 | 42 | 10:00 | 57 | 19:00 | 166 | 19:00 | 32 | 19:00 | 67 | 18:00 | 22 | 18:00 | 59 | 14:00 | 80 | 18:00 | 231 | 18:00 | 162 | 18:30 | 69 | 18:00
31 | 341 | 18:00 |  |  |  |  | 20 | 18:00 | 17.6 | 10:00 | 1.3 | 4:00 | 185 | 18:00 | 547 | 18:00 | 164 | 18:00 | 171 | 17:30 | 223 | 18:00 | 39 | 9:00 | 55 | 12:00 | 156 | 12:00 | 34 | 6:00 | 70 | 18:30 | 22 | 19:30 | 58 | 10:00 | 84 | 18:00 | 237 | 18:00 | 167 | 18:00 | 72 | 18:00
32
Monthly | 435 |  | 0 |  | 0 |  | 105 |  | 26.7 |  | 1.7 |  | 214 |  | 589 |  | 178 |  | 171 |  | 255 |  | 48 |  | 144 |  | 331 |  | 39 |  | 141 |  | 57 |  | 61 |  | 134 |  | 376 |  | 270 |  | 189
…………….. …………….. ……………..
Prepared by Checked by Approved by

## Kartik
NEPAL ELECTRICITY AUTHORITY
DHARAN DISTRIBUTION CENTER
Peak Load Details
Month: | Kartik | 2082
Day | 33KV Duhabi-Dharan |  |  |  | 33KV Dharan-Dhankuta |  |  |  | 33KV Dharan-Chatara Bayarban |  |  |  | 33/11KV, 16.6MVA Power Trf 1 |  | 11KV Incomer 1 |  | Dharan |  | Bagarkot |  | Local Chatara |  | BPKIHS |  | 33/11KV, 8MVA Power Trf 2 |  | 11KV Incomer 2 |  | Khanepani |  | Railway |  | British |  | Industrial |  | 33/11KV, 8MVA Power Trf 3 |  | 11KV Incomer 3 |  | Bhanu |  | Panmara
| Max. Import (A) | Time | Max. Export (A) | Time | Max. Import (A) | Time | Max. Export (A) | Time | Max. Import (A) | Time | Max. Export (A) | Time | Max. (A) | Time | Max. (A) | Time | Max. (A) | Time | Max. (A) | Time | Max. (A) | Time | Max. (A) | Time | Max. (A) | Time | Max. (A) | Time | Max. (A) | Time | Max. (A) | Time | Max. (A) | Time | Max. (A) | Time | Max. (A) | Time | Max. (A) | Time | Max. (A) | Time | Max. (A) | Time
1 | 331 | 18:30 |  |  |  |  | 56 | 9:00 | 18.3 | 13:00 |  |  | 180 | 18:30 | 542 | 18:30 | 169 | 18:30 | 149 | 18:30 | 236 | 18:30 | 23 | 8:00 | 48 | 18:30 | 142 | 18:30 | 34 | 15:00 | 73 | 18:30 | 22 | 19:00 | 25 | 11:00 | 81 | 18:30 | 241 | 18:30 | 184 | 19:00 | 65 | 18:30
2 | 346 | 18:30 |  |  |  |  | 25 | 18:30 | 16.1 | 8:00 |  |  | 196 | 18:30 | 549 | 18:30 | 167 | 18:30 | 152 | 18:30 | 227 | 18:30 | 41 | 9:00 | 52 | 18:30 | 138 | 18:30 | 35 | 7:00 | 69 | 18:30 | 19 | 19:30 | 43 | 9:00 | 88 | 18:00 | 226 | 18:00 | 163 | 18:00 | 62 | 18:00
3 | 343 | 19:00 |  |  |  |  | 22 | 19:00 | 14.6 | 4:00 |  |  | 197 | 18:30 | 581 | 18:30 | 174 | 18:00 | 164 | 18:00 | 244 | 18:30 | 22 | 10:00 | 54 | 18:00 | 143 | 18:00 | 32 | 12:00 | 69 | 18:30 | 19 | 18:00 | 11 | 14:00 | 86 | 18:30 | 234 | 18:30 | 171 | 18:30 | 66 | 18:30
4 | 319 | 18:30 |  |  |  |  | 20 | 18:30 | 17.8 | 15:00 |  |  | 192 | 18:00 | 562 | 18:00 | 169 | 18:00 | 157 | 18:30 | 239 | 18:30 | 22 | 9:00 | 52 | 18:30 | 147 | 18:30 | 35 | 7:00 | 76 | 18:00 | 19 | 19:00 | 8 | 18:30 | 78 | 18:00 | 218 | 18:00 | 158 | 18:00 | 67 | 18:00
5 | 320 | 18:00 |  |  |  |  | 20 | 18:30 | 15 | 18:00 |  |  | 184 | 18:00 | 540 | 18:00 | 158 | 18:00 | 146 | 18:00 | 229 | 18:00 | 21 | 8:00 | 49 | 18:30 | 141 | 18:30 | 31 | 17:30 | 71 | 18:00 | 19 | 18:30 | 10 | 11:00 | 75 | 18:00 | 210 | 18:00 | 151 | 18:30 | 65 | 18:00
6 | 300 | 18:30 |  |  |  |  | 19 | 18:30 | 13.7 | 18:00 |  |  | 179 | 18:00 | 516 | 18:00 | 142 | 18:00 | 148 | 18:00 | 212 | 19:00 | 21 | 10:00 | 34 | 18:30 | 102 | 18:30 | 34 | 7:00 | 70 | 18:30 | 18 | 18:00 | 5 | 1:00 | 68 | 18:00 | 185 | 18:00 | 121 | 18:30 | 64 | 18:30
7 | 305 | 18:00 |  |  |  |  | 20 | 18:00 | 15.4 | 14:00 |  |  | 171 | 18:00 | 505 | 18:00 | 147 | 18:00 | 144 | 18:00 | 214 | 18:00 | 33 | 10:00 | 48 | 18:30 | 130 | 18:30 | 38 | 16:00 | 70 | 18:00 | 19 | 19:00 | 7 | 6:00 | 70 | 18:30 | 196 | 18:00 | 134 | 18:30 | 63 | 18:00
8 | 324 | 18:00 |  |  |  |  | 24 | 18:00 | 7.9 | 3:00 | 1.2 | 18:00 | 173 | 18:00 | 511 | 18:00 | 149 | 18:00 | 143 | 18:30 | 216 | 18:00 | 21 | 9:00 | 43 | 14:00 | 122 | 14:00 | 39 | 15:00 | 69 | 18:30 | 18 | 19:30 | 8 | 10:00 | 73 | 18:00 | 204 | 18:00 | 141 | 18:00 | 62 | 18:00
9 | 331 | 18:00 |  |  |  |  | 24 | 18:00 |  |  | 1.1 | 17:30 | 189 | 18:30 | 536 | 18:30 | 160 | 18:30 | 146 | 18:30 | 219 | 18:30 | 36 | 9:00 | 50 | 16:00 | 139 | 16:00 | 38 | 5:00 | 66 | 18:00 | 19 | 19:00 | 38 | 16:00 | 77 | 18:30 | 216 | 18:30 | 156 | 18:30 | 62 | 18:00
10 | 306 | 18:00 |  |  |  |  | 20 | 18:00 |  |  | 1.1 | 18:00 | 162 | 18:30 | 494 | 18:30 | 150 | 18:30 | 136 | 18:30 | 208 | 18:30 | 31 | 12:00 | 50 | 11:00 | 150 | 11:00 | 38 | 6:00 | 65 | 18:00 | 18 | 20:00 | 41 | 12:00 | 69 | 18:00 | 197 | 18:00 | 137 | 18:00 | 58 | 18:00
11 | 308 | 18:00 |  |  |  |  | 20 | 18:00 | 13.3 | 16:00 | 1 | 2:00 | 173 | 18:00 | 506 | 18:00 | 153 | 18:00 | 139 | 18:00 | 209 | 18:00 | 37 | 9:00 | 53 | 8:00 | 139 | 8:00 | 39 | 6:00 | 59 | 18:00 | 22 | 19:00 | 37 | 10:00 | 74 | 18:00 | 208 | 18:00 | 146 | 18:00 | 60 | 18:00
12 | 295 | 18:00 |  |  |  |  | 21 | 18:00 | 12 | 18:00 | 1 | 1:00 | 161 | 18:00 | 472 | 18:00 | 143 | 18:00 | 132 | 18:00 | 194 | 18:00 | 38 | 10:00 | 49 | 8:00 | 143 | 8:00 | 38 | 8:00 | 61 | 18:00 | 22 | 19:30 | 44 | 10:00 | 70 | 18:00 | 197 | 18:00 | 141 | 17:30 | 54 | 18:00
13 | 368 | 18:00 |  |  |  |  | 75 | 18:00 | 10.9 | 18:00 |  |  | 155 | 18:00 | 461 | 18:00 | 133 | 18:00 | 126 | 18:00 | 192 | 18:00 | 34 | 10:00 | 51 | 17:30 | 144 | 17:30 | 38 | 7:00 | 56 | 18:00 | 20 | 18:00 | 36 | 9:00 | 65 | 18:00 | 184 | 18:00 | 130 | 18:00 | 53 | 18:00
14 | 352 | 18:00 |  |  |  |  | 90 | 18:00 | 11 | 4:00 | 1.1 | 18:00 | 145 | 18:00 | 431 | 18:00 | 130 | 18:00 | 118 | 18:00 | 180 | 18:00 | 29 | 13:00 | 48 | 17:30 | 133 | 17:30 | 35 | 17:00 | 59 | 18:00 | 19 | 18:30 | 36 | 13:00 | 61 | 18:00 | 173 | 18:00 | 122 | 17:30 | 51 | 18:00
15 | 344 | 18:00 |  |  |  |  | 82 | 18:00 |  |  | 1 | 7:00 | 143 | 18:00 | 431 | 18:00 | 129 | 17:30 | 116 | 17:30 | 176 | 18:30 | 17 | 11:00 | 45 | 18:00 | 131 | 18:00 | 35 | 7:00 | 62 | 17:30 | 20 | 20:00 | 12 | 18:00 | 59 | 18:00 | 179 | 18:00 | 119 | 17:30 | 56 | 18:00
16 | 369 | 18:30 |  |  |  |  | 88 | 18:30 |  |  | 1.3 | 18:30 | 169 | 18:00 | 468 | 18:30 | 141 | 18:00 | 125 | 18:00 | 189 | 18:30 | 27 | 12:00 | 50 | 8:00 | 139 | 8:00 | 36 | 7:00 | 63 | 18:30 | 21 | 19:00 | 48 | 15:00 | 75 | 17:30 | 214 | 17:30 | 156 | 17:30 | 56 | 17:30
17 | 291 | 18:00 |  |  |  |  | 58 | 9:00 |  |  | 1.2 | 7:00 | 179 | 18:00 | 523 | 18:00 | 138 | 18:00 | 126 | 18:00 | 229 | 18:00 | 46 | 12:00 | 30 | 19:00 | 87 | 19:00 | 7 | 5:00 | 52 | 19:00 | 20 | 8:00 | 45 | 11:00 | 65 | 18:00 | 175 | 18:00 | 121 | 18:00 | 53 | 18:00
18 | 301 | 18:30 |  |  |  |  | 22 | 18:00 |  |  | 1.2 | 7:00 | 162 | 18:00 | 485 | 18:00 | 149 | 18:00 | 128 | 18:00 | 197 | 18:00 | 32 | 9:00 | 52 | 17:30 | 148 | 17:30 | 34 | 17:00 | 62 | 18:00 | 20 | 18:30 | 54 | 11:00 | 72 | 18:00 | 200 | 18:00 | 142 | 18:00 | 58 | 18:00
19 | 305 | 18:00 |  |  |  |  | 21 | 19:30 |  |  | 1.1 | 18:30 | 163 | 18:00 | 483 | 18:00 | 146 | 18:00 | 131 | 18:00 | 199 | 18:00 | 32 | 10:00 | 53 | 8:00 | 149 | 8:00 | 44 | 7:00 | 64 | 18:00 | 22 | 18:30 | 54 | 10:00 | 69 | 17:30 | 194 | 17:30 | 137 | 17:30 | 56 | 18:00
20 | 322 | 18:00 |  |  |  |  | 21 | 18:00 |  |  | 1.1 | 7:00 | 169 | 18:00 | 497 | 18:00 | 155 | 18:00 | 135 | 18:00 | 202 | 18:00 | 34 | 11:00 | 54 | 17:30 | 153 | 17:30 | 36 | 18:00 | 66 | 18:00 | 21 | 18:00 | 52 | 11:00 | 73 | 18:00 | 204 | 18:00 | 144 | 18:30 | 59 | 18:30
21 | 310 | 17:30 |  |  |  |  | 21 | 18:00 |  |  | 1.1 | 10:00 | 157 | 18:00 | 475 | 18:00 | 146 | 17:30 | 130 | 18:00 | 190 | 18:00 | 33 | 10:00 | 50 | 7:00 | 150 | 7:00 | 32 | 13:00 | 62 | 17:30 | 20 | 19:00 | 56 | 14:00 | 69 | 18:00 | 193 | 18:00 | 137 | 18:00 | 57 | 17:30
22 | 296 | 18:00 |  |  |  |  | 21 | 18:00 |  |  | 1.4 | 18:00 | 160 | 18:00 | 460 | 18:00 | 143 | 18:00 | 125 | 18:00 | 191 | 18:00 | 21 | 11:00 | 49 | 18:30 | 129 | 18:30 | 39 | 8:00 | 61 | 18:00 | 20 | 19:00 | 30 | 11:00 | 68 | 14:00 | 188 | 14:00 | 126 | 17:30 | 55 | 18:00
23 | 319 | 18:00 |  |  |  |  | 24 | 18:00 |  |  | 1.2 | 18:00 | 166 | 18:00 | 471 | 18:00 | 153 | 18:00 | 131 | 18:00 | 192 | 18:00 | 33 | 11:00 | 52 | 8:00 | 152 | 8:00 | 39 | 3:00 | 67 | 18:00 | 20 | 18:30 | 60 | 9:00 | 78 | 17:30 | 196 | 17:30 | 141 | 17:30 | 56 | 17:30
24 | 299 | 18:00 |  |  |  |  | 20 | 18:00 |  |  | 1.3 | 7:00 | 151 | 18:00 | 442 | 18:00 | 135 | 18:00 | 118 | 18:00 | 183 | 18:00 | 36 | 11:00 | 52 | 18:00 | 147 | 18:00 | 32 | 18:30 | 56 | 18:00 | 20 | 7:00 | 58 | 11:00 | 63 | 18:00 | 175 | 18:00 | 120 | 18:00 | 53 | 18:00
25 | 300 | 18:00 |  |  |  |  | 20 | 18:00 |  |  | 1.2 | 11:00 | 149 | 18:00 | 440 | 18:00 | 137 | 18:00 | 118 | 18:00 | 177 | 18:00 | 32 | 8:00 | 66 | 18:00 | 165 | 18:00 | 32 | 8:00 | 110 | 17:30 | 20 | 18:00 | 58 | 9:00 | 61 | 17:30 | 172 | 17:30 | 117 | 17:30 | 55 | 18:00
26 | 296 | 18:00 |  |  |  |  | 20 | 18:30 |  |  | 1.2 | 18:00 | 148 | 18:00 | 434 | 18:00 | 133 | 18:00 | 117 | 18:00 | 174 | 18:00 | 30 | 13:00 | 57 | 18:00 | 167 | 18:00 | 36 | 7:00 | 99 | 18:00 | 19 | 18:00 | 48 | 10:00 | 62 | 18:00 | 175 | 18:00 | 123 | 18:00 | 50 | 18:00
27 | 280 | 18:00 |  |  |  |  | 18 | 18:00 |  |  | 1.5 | 6:00 | 144 | 18:00 | 426 | 18:00 | 130 | 18:00 | 116 | 18:00 | 169 | 18:00 | 30 | 10:00 | 58 | 8:00 | 162 | 9:00 | 43 | 8:00 | 55 | 6:00 | 19 | 7:00 | 54 | 9:00 | 60 | 17:30 | 170 | 17:30 | 118 | 17:30 | 50 | 18:00
28 | 284 | 18:00 |  |  |  |  | 21 | 18:00 |  |  | 1.2 | 8:00 | 143 | 18:00 | 424 | 18:00 | 128 | 18:00 | 114 | 18:00 | 171 | 18:00 | 28 | 9:00 | 48 | 10:00 | 138 | 10:00 | 34 | 10:00 | 57 | 18:00 | 18 | 7:00 | 53 | 9:00 | 62 | 18:00 | 172 | 18:00 | 122 | 17:30 | 50 | 18:00
29 | 349 | 18:00 |  |  |  |  | 85 | 18:00 |  |  | 1.2 | 18:30 | 142 | 18:00 | 437 | 18:00 | 137 | 18:00 | 121 | 18:00 | 180 | 18:30 | 45 | 8:00 | 48 | 17:30 | 136 | 17:30 | 45 | 8:00 | 59 | 18:00 | 19 | 18:00 | 32 | 12:00 | 62 | 18:00 | 189 | 18:00 | 150 | 18:30 | 56 | 18:00
30 | 371 | 18:00 |  |  |  |  | 91 | 18:00 |  |  | 1.3 | 8:00 | 153 | 18:00 | 454 | 18:00 | 139 | 17:30 | 119 | 18:00 | 177 | 18:00 | 31 | 15:00 | 52 | 17:30 | 146 | 17:30 | 34 | 7:00 | 62 | 17:30 | 19 | 7:00 | 59 | 9:00 | 69 | 17:30 | 189 | 17:30 | 131 | 17:30 | 55 | 17:30
31
32
Monthly | 371 |  | 0 |  | 0 |  | 91 |  | 18.3 |  | 1.5 |  | 197 |  | 581 |  | 174 |  | 164 |  | 244 |  | 46 |  | 66 |  | 167 |  | 45 |  | 110 |  | 22 |  | 60 |  | 88 |  | 241 |  | 184 |  | 67
Note: 11kV BPKIHS Feeder , British Feeder & Khanepani is supplied from 33kV Chatara/ IPP Transmission Line that the Power imported from hydropower situated at Sankhuwasabha & Tehrathum by Operating in Isolated Mode during 33kV line intruption from Duhabi Grid due to Flood entered at Grid Area on Dated 2078-07-03 & 2078-07-04
…………….. …………….. ……………..
Prepared by Checked by Approved by

## aiakh (hidden)
NEPAL ELECTRICITY AUTHORITY
DHARAN DISTRIBUTION CENTER
Peak Load Details
Month: | Chaitra | 2078
Day | 33KV Duhabi-Dharan |  |  |  | 33KV Dharan-Dhankuta |  |  |  | 33KV Dharan-Chatara Bayarban |  |  |  | 33/11KV, 16.6MVA Power Trf 1 |  | 11KV Incomer 1 |  | Dharan |  | Local Chatara |  | Panmara |  | BPKIHS |  | 33/11KV, 8MVA Power Trf 2 |  | 11KV Incomer 2 |  | Railway |  | Khanepani |  | British |  | Industrial |  | 33/11KV, 8MVA Power Trf 3 |  | 11KV Incomer 3 |  | Bhanu
| Max. Import (A) | Time | Max. Export (A) | Time | Max. Import (A) | Time | Max. Export (A) | Time | Max. Import (A) | Time | Max. Export (A) | Time | Max. (A) | Time | Max. (A) | Time | Max. (A) | Time | Max. (A) | Time | Max. (A) | Time | Max. (A) | Time | Max. (A) | Time | Max. (A) | Time | Max. (A) | Time | Max. (A) | Time | Max. (A) | Time | Max. (A) | Time | Max. (A) | Time | Max. (A) | Time | Max. (A) | Time
1 | 330 | 19:00 |  |  |  |  | 61 | 19:00 | 57 | 12:00 | 30 | 19:00 | 170 | 19:00 | 493 | 19:00 | 117 | 19:00 | 188 | 19:00 | 173 | 19:00 | 37 | 15:00 | 66 | 8:00 | 188 | 8:00 | 53 | 19:00 | 75 | 7:00 | 27 | 19:30 | 61 | 9:00 | 45 | 18:30 | 132 | 18:30 | 132 | 18:30
2 | 332 | 19:00 |  |  |  |  | 64 | 19:00 | 58 | 13:00 | 28 | 19:00 | 171 | 19:00 | 499 | 19:00 | 119 | 19:00 | 191 | 19:00 | 167 | 19:00 | 40 | 11:00 | 58 | 10:00 | 177 | 10:00 | 52 | 19:00 | 66 | 19:30 | 26 | 19:30 | 59 | 10:00 | 45 | 19:00 | 128 | 19:00 | 128 | 19:00
3 | 292 | 19:00 |  |  |  |  | 57 | 19:00 | 71 | 14:00 |  |  | 167 | 19:00 | 484 | 19:00 | 115 | 19:00 | 190 | 19:00 | 159 | 19:00 | 37 | 10:00 | 58 | 9:00 | 167 | 9:00 | 49 | 19:00 | 78 | 19:00 | 25 | 19:30 | 44 | 9:00 | 44 | 19:00 | 127 | 19:00 | 127 | 19:00
4 | 283 | 19:00 |  |  |  |  | 61 | 19:00 | 63 | 11:00 |  |  | 163 | 19:00 | 467 | 19:00 | 102 | 19:00 | 183 | 19:00 | 172 | 19:00 | 21 | 12:00 | 51 | 480:00 | 147 | 20:00 | 50 | 19:00 | 72 | 7:00 | 25 | 19:00 | 6 | 16:00 | 38 | 19:00 | 111 | 19:00 | 111 | 19:00
5 | 393 | 19:30 |  |  |  |  | 108 | 19:00 | 59 | 1:00 | 41 | 19:30 | 204 | 18:00 | 584 | 18:00 | 163 | 17:30 | 227 | 19:30 | 199 | 18:00 | 19 | 8:00 | 56 | 17:30 | 158 | 17:30 | 62 | 18:00 | 75 | 17:30 | 29 | 20:00 | 7 | 19:30 | 68 | 17:30 | 188 | 17:30 | 188 | 17:30
6 | 355 | 19:00 |  |  |  |  | 69 | 19:00 | 65 | 12:00 | 30 | 11:00 | 191 | 19:00 | 558 | 19:00 | 139 | 19:00 | 200 | 19:00 | 198 | 19:00 | 40 | 12:00 | 64 | 18:30 | 198 | 18:30 | 60 | 19:00 | 82 | 18:30 | 31 | 19:30 | 44 | 13:00 | 55 | 19:00 | 153 | 19:00 | 153 | 19:00
7 | 294 | 19:00 |  |  |  |  | 46 | 18:00 | 76 | 12:00 | 22 | 19:00 | 170 | 19:00 | 508 | 19:00 | 130 | 18:30 | 201 | 20:00 | 175 | 19:00 | 43 | 12:00 | 62 | 17:30 | 183 | 17:30 | 49 | 18:30 | 77 | 18:30 | 32 | 20:00 | 44 | 11:00 | 45 | 18:30 | 131 | 18:30 | 131 | 18:30
8 | 285 | 18:30 |  |  |  |  | 48 | 19:30 | 130 | 21:00 | 46 | 17:30 | 152 | 18:30 | 441 | 18:30 | 126 | 18:30 | 175 | 19:00 | 120 | 18:30 | 39 | 12:00 | 63 | 17:00 | 193 | 17:00 | 50 | 18:30 | 80 | 17:00 | 29 | 19:30 | 50 | 13:00 | 68 | 18:30 | 206 | 18:30 | 206 | 18:30
9 | 301 | 19:00 |  |  |  |  | 56 | 19:30 | 98 | 1:00 |  |  | 160 | 19:00 | 460 | 19:00 | 139 | 19:00 | 181 | 19:00 | 127 | 19:00 | 41 | 11:00 | 65 | 19:00 | 189 | 19:00 | 50 | 19:00 | 83 | 16:00 | 31 | 19:30 | 54 | 9:00 | 72 | 19:00 | 207 | 19:00 | 207 | 19:00
10 | 309 | 19:00 |  |  |  |  | 79 | 19:30 | 98 | 12:00 |  |  | 153 | 19:00 | 443 | 19:00 | 132 | 19:00 | 174 | 19:00 | 115 | 19:00 | 44 | 11:00 | 65 | 16:00 | 201 | 16:00 | 19:00 | 19:00 | 78 | 8:00 | 29 | 19:30 | 61 | 16:00 | 68 | 19:00 | 196 | 19:00 | 196 | 19:00
11 | 280 | 19:30 |  |  |  |  | 46 | 20:00 | 89 | 12:00 |  |  | 156 | 19:00 | 447 | 19:00 | 126 | 19:00 | 178 | 19:00 | 122 | 19:00 | 43 | 11:00 | 65 | 16:00 | 194 | 16:00 | 49 | 19:00 | 78 | 17:00 | 27 | 19:00 | 60 | 16:00 | 69 | 19:00 | 195 | 19:00 | 195 | 19:00
12 | 325 | 19:30 |  |  |  |  | 59 | 18:30 | 77 | 11:00 |  |  | 168 | 18:30 | 488 | 18:30 | 160 | 18:00 | 207 | 18:30 | 131 | 19:30 | 24 | 12:00 | 60 | 19:30 | 176 | 19:30 | 58 | 19:00 | 78 | 19:30 | 26 | 19:30 | 28 | 9:00 | 83 | 18:30 | 246 | 18:30 | 246 | 18:30
13 | 310 | 19:00 |  |  |  |  | 63 | 19:00 | 84 | 13:00 | 19 | 11:00 | 149 | 19:30 | 427 | 19:30 | 134 | 19:00 | 182 | 19:00 | 116 | 19:30 | 39 | 12:00 | 66 | 16:00 | 190 | 16:00 | 50 | 19:00 | 77 | 6:00 | 29 | 19:00 | 61 | 10:00 | 68 | 19:00 | 195 | 19:00 | 195 | 19:00
14 | 304 | 19:00 |  |  |  |  | 57 | 19:00 | 81 | 24:00 |  |  | 142 | 19:00 | 413 | 19:00 | 120 | 19:00 | 168 | 19:00 | 107 | 19:00 | 41 | 10:00 | 70 | 12:00 | 197 | 12:00 | 51 | 19:00 | 80 | 13:00 | 30 | 20:00 | 71 | 16:00 | 61 | 19:00 | 180 | 19:00 | 180 | 19:00
15 | 258 | 19:00 |  |  |  |  | 57 | 19:00 | 84 | 12:00 |  |  | 137 | 19:00 | 400 | 19:00 | 118 | 19:00 | 165 | 19:00 | 100 | 19:00 | 41 | 11:00 | 64 | 11:00 | 188 | 11:00 | 48 | 19:00 | 77 | 13:00 | 28 | 19:00 | 67 | 16:00 | 60 | 19:00 | 174 | 19:00 | 174 | 19:00
16 | 250 | 19:00 |  |  |  |  | 67 | 8:00 | 100 | 10:00 | 10 | 15:00 | 142 | 19:00 | 409 | 19:00 | 120 | 19:00 | 170 | 19:00 | 105 | 19:00 | 41 | 11:00 | 65 | 9:00 | 194 | 9:00 | 48 | 19:00 | 78 | 8:00 | 28 | 20:00 | 63 | 9:00 | 63 | 19:00 | 182 | 19:00 | 182 | 19:00
17 | 280 | 19:30 |  |  |  |  | 49 | 9:00 | 115 | 24:00 |  |  | 140 | 19:00 | 415 | 20:00 | 125 | 20:00 | 170 | 20:00 | 104 | 20:00 | 41 | 10:00 | 63 | 8:00 | 184 | 8:00 | 51 | 19:00 | 76 | 9:00 | 28 | 19:30 | 60 | 14:00 | 65 | 20:00 | 181 | 20:00 | 181 | 20:00
18 | 217 | 19:30 |  |  |  |  | 70 | 11:00 | 182 | 9:00 |  |  | 133 | 19:00 | 389 | 19:00 | 111 | 19:00 | 157 | 19:00 | 98 | 19:00 | 41 | 10:00 | 66 | 9:00 | 191 | 9:00 | 50 | 19:00 | 74 | 18:30 | 26 | 19:30 | 62 | 9:00 | 58 | 19:00 | 169 | 19:00 | 169 | 19:00
19 | 262 | 15:00 | 135 | 23:00 | 72 | 23:00 | 42 | 6:00 | 195 | 23:00 |  |  | 150 | 19:00 | 430 | 19:00 | 131 | 19:00 | 177 | 19:00 | 106 | 19:00 | 24 | 16:00 | 50 | 21:00 | 142 | 21:00 | 48 | 18:30 | 72 | 6:00 | 28 | 19:30 | 13 | 6:00 | 69 | 15:00 | 199 | 15:00 | 199 | 15:00
20 | 204 | 19:30 | 177 | 4:00 | 102 | 4:00 | 56 | 19:30 | 194 | 4:00 |  |  | 136 | 19:00 | 398 | 19:00 | 114 | 18:30 | 159 | 19:00 | 103 | 19:00 | 37 | 16:00 | 62 | 11:00 | 182 | 11:00 | 49 | 19:00 | 74 | 19:00 | 26 | 20:00 | 64 | 14:00 | 57 | 19:00 | 166 | 19:00 | 166 | 19:00
21 | 217 | 8:00 |  |  | 35 | 15:00 | 63 | 8:00 | 120 | 1:00 | 31 | 14:00 | 156 | 19:00 | 448 | 19:00 | 123 | 19:00 | 188 | 19:00 | 117 | 19:00 | 40 | 12:00 | 64 | 8:00 | 190 | 8:00 | 55 | 19:00 | 76 | 8:00 | 31 | 19:30 | 66 | 9:00 | 67 | 19:00 | 192 | 19:00 | 192 | 19:00
22 | 254 | 19:30 |  |  | 27 | 3:00 | 63 | 19:30 | 114 | 11:00 |  |  | 151 | 19:00 | 440 | 19:00 | 133 | 19:30 | 183 | 19:00 | 112 | 19:00 | 40 | 9:00 | 68 | 10:00 | 201 | 10:00 | 53 | 19:00 | 76 | 16:00 | 29 | 19:00 | 71 | 10:00 | 67 | 19:00 | 194 | 19:00 | 194 | 19:00
23 | 229 | 20:00 | 99 | 23:00 | 17 | 23:00 | 40 | 19:00 | 202 | 23:00 |  |  | 147 | 19:00 | 427 | 19:00 | 128 | 19:00 | 180 | 19:00 | 109 | 19:00 | 39 | 10:00 | 70 | 7:00 | 209 | 7:00 | 63 | 7:00 | 75 | 7:00 | 31 | 19:30 | 55 | 9:00 | 68 | 19:00 | 189 | 19:00 | 189 | 19:00
24 | 199 | 19:30 | 138 | 24:00 | 36 | 24:00 | 58 | 19:30 | 232 | 24:00 |  |  | 142 | 19:00 | 403 | 19:00 | 121 | 19:00 | 165 | 19:00 | 97 | 19:00 | 43 | 13:00 | 68 | 8:00 | 193 | 8:00 | 48 | 19:30 | 77 | 9:00 | 28 | 20:00 | 69 | 13:00 | 59 | 19:00 | 172 | 19:00 | 172 | 19:00
25 | 288 | 19:00 | 107 | 2:00 | 36 | 4:00 | 62 | 9:00 | 190 | 1:00 |  |  | 150 | 19:00 | 431 | 19:00 | 128 | 19:00 | 180 | 19:00 | 112 | 19:00 | 38 | 11:00 | 72 | 8:00 | 204 | 8:00 | 51 | 19:30 | 81 | 22:00 | 26 | 19:30 | 66 | 8:00 | 67 | 19:00 | 192 | 19:00 | 192 | 19:00
26 | 202 | 8:00 | 126 | 23:00 | 110 | 22:00 | 71 | 8:00 | 238 | 9:00 |  |  | 131 | 19:00 | 366 | 19:00 | 110 | 19:00 | 151 | 19:00 | 94 | 19:00 | 18 | 11:00 | 59 | 8:00 | 163 | 8:00 | 50 | 19:00 | 80 | 13:00 | 27 | 20:00 | 33 | 8:00 | 56 | 19:00 | 165 | 19:00 | 165 | 19:00
27 | 172 | 12:00 | 315 | 18:30 | 126 | 16:00 | 30 | 12:00 | 360 | 18:30 |  |  | 133 | 19:00 | 376 | 19:00 | 116 | 19:00 | 150 | 19:00 | 95 | 19:00 | 35 | 11:00 | 60 | 8:00 | 174 | 8:00 | 47 | 19:00 | 79 | 6:00 | 25 | 19:30 | 44 | 12:00 | 56 | 19:00 | 158 | 19:00 | 158 | 19:00
28 | 128 | 7:00 | 315 | 8:00 | 117 | 3:00 | 28 | 6:00 | 374 | 8:00 |  |  | 141 | 19:00 | 410 | 19:00 | 119 | 19:00 | 165 | 19:00 | 102 | 19:00 | 38 | 13:00 | 68 | 12:00 | 199 | 12:00 | 50 | 19:00 | 82 | 18:30 | 26 | 19:30 | 67 | 13:00 | 61 | 19:00 | 175 | 19:00 | 175 | 19:00
29 | 165 | 8:00 | 182 | 3:00 | 65 | 1:00 | 24 | 19:30 | 237 | 2:00 |  |  | 152 | 19:00 | 447 | 19:00 | 140 | 19:00 | 178 | 19:00 | 111 | 19:00 | 38 | 11:00 | 74 | 11:00 | 206 | 11:00 | 56 | 19:00 | 83 | 18:30 | 29 | 20:00 | 65 | 11:00 | 76 | 19:00 | 227 | 19:00 | 227 | 19:00
30 | 235 | 20:00 | 130 | 10:00 | 37 | 13:00 | 22 | 19:00 | 184 | 1:00 |  |  | 149 | 19:00 | 430 | 19:00 | 131 | 19:00 | 171 | 19:00 | 108 | 19:00 | 42 | 18:30 | 67 | 8:00 | 198 | 8:00 | 55 | 19:00 | 83 | 11:00 | 26 | 19:00 | 58 | 8:00 | 68 | 19:00 | 195 | 19:00 | 195 | 19:00
31
32
Monthly | 393 |  | 315 |  | 126 |  | 108 |  | 374 |  | 46 |  | 204 |  | 584 |  | 163 |  | 227 |  | 199 |  | 44 |  | 74 |  | 209 |  | 63 |  | 83 |  | 32 |  | 71 |  | 83 |  | 246 |  | 246
…………….. …………….. ……………..
Prepared by Checked by Approved by

## Peak Summary(33 kV)
2081/082 | 33kV Duhabi |  | 33KV Dhankuta |  | 33KV Chatara Bayarban |  | 16.6 MVA Trf 1 |  | 6/8 MVA Trf 2 |  | 6/8 MVA Trf 3 |  | S/S Max. Load |  | S/S Max. Load Of 2080/081
| Import | Export | Import | Export | Import | Export | A | MVA | A | MVA | A | MVA | A | MVA | A | MVA
Shrawan | 444 | 0 | 0 | 52 | 23 | 6.1 | 239 | 13.4554 | 79 | 4.4476 | 98 | 5.5173 | 416 | 23.4202 | 394 | 22.1817
Bhadra | 382 | 0 | 0 | 50 | 36 | 0 | 220 | 12.3857 | 78 | 4.3913 | 90 | 5.0669 | 388 | 21.8439 | 384 | 21.6187
Ashoj | 435 | 0 | 0 | 105 | 26.7 | 1.7 | 214 | 12.0479 | 144 | 8.107 | 134 | 7.544 | 492 | 27.6989 | 366 | 20.6053
Kartik | 371 | 0 | 0 | 91 | 18.3 | 1.5 | 197 | 11.0908 | 66 | 3.7157 | 88 | 4.9543 | 351 | 19.7608 | 307 | 17.2837
Mangsir | [14 empty] | 318 | 17.903
Poush | [14 empty] | 280 | 15.7636
Magh | [14 empty] | 289 | 16.2703
Falgun | [14 empty] | 289 | 16.2703
Chaitra | [14 empty] | 355 | 19.986
Baisakh | [14 empty] | 390 | 21.9565
Jestha | [14 empty] | 423 | 23.8143
Asadh | [14 empty] | 366 | 20.6053
Yearly